## Legend
Change
Deleted
Revise tag / addition tag | The coloring is marked up with respect to Rec 00C IO list file which shared to Emerson on Jul 25th. 2002

## Filtered IO
PID | Tag Number | Loop Name | Location | Instrument Type | Service | Calibration Range Min | Calibration Range Max | Calibration Range Units | DCS Range Min | DCS Range Max | DCS Range Units | Alarm High | Alarm High High | High High Trip | Alarm Low | Alarm Low Low | Low Low Trip | Alarm Units | Equipment Name | I/O Type Name | Controller No. | Signal Type | System Type | Device Protocol | Power Supply | Remarks | Rev
CA-741752-001 | 631-AY -3054 | 631-A-3054 | VALVE | SOLENOID VALVE | 631-D-0304A DSL FUEL FLTR DRN VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XSH -3054 | 631-A-3054 | VALVE | VALVE POSITION SWITCH OPEN | 631-D-0304A DSL FUEL FLTR DRN VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XSL -3054 | 631-A-3054 | VALVE | VALVE POSITION SWITCH CLOSED | 631-D-0304A DSL FUEL FLTR DRN VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XIH -3054 | 631-A-3054 | DCS | STATUS INDICATION OPEN | 631-D-0304A DSL FUEL FLTR DRN VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XIL -3054 | 631-A-3054 | DCS | STATUS INDICATION CLOSED | 631-D-0304A DSL FUEL FLTR DRN VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3054A | 631-A-3054 | DCS | DCS HAND SWITCH VALVE OPEN | 631-D-0304A DSL FUEL FLTR DRN OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3054B | 631-A-3054 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-D-0304A DSL FUEL FLTR DRN CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XA -3054 | 631-A-3054 | DCS | FAULT ALARM/TRIP INDICATION | 631-D-0304A DSL FUEL FLTR DRN FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-AY -3055 | 631-A-3055 | VALVE | SOLENOID VALVE | 631-D-0304B DSL FUEL FLTR DRN VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XSH -3055 | 631-A-3055 | VALVE | VALVE POSITION SWITCH OPEN | 631-D-0304B DSL FUEL FLTR DRN VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XSL -3055 | 631-A-3055 | VALVE | VALVE POSITION SWITCH CLOSED | 631-D-0304B DSL FUEL FLTR DRN VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XIH -3055 | 631-A-3055 | DCS | STATUS INDICATION OPEN | 631-D-0304B DSL FUEL FLTR DRN VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XIL -3055 | 631-A-3055 | DCS | STATUS INDICATION CLOSED | 631-D-0304B DSL FUEL FLTR DRN VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3055A | 631-A-3055 | DCS | DCS HAND SWITCH VALVE OPEN | 631-D-0304B DSL FUEL FLTR DRN OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3055B | 631-A-3055 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-D-0304B DSL FUEL FLTR DRN CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XA -3055 | 631-A-3055 | DCS | FAULT ALARM/TRIP INDICATION | 631-D-0304B DSL FUEL FLTR DRN FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-FIT -3051 | 631-F-3051 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-D-0305 DSL FUEL TNK INL FLO | 0 | 100 | inH2O | 0 | 110 | US gal/min | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-FQI -3051 | 631-F-3051 | DCS | FLOW TOTALIZING INDICATOR | 631-D-0305 DSL FUEL TNK INL FLO TOT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-FIT -3052 | 631-F-3052 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0306A/B DSL FUEL PMP DISCH FLO | 0 | 100 | inH2O | 0 | 45 | US gal/min | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-FIC -3052 | 631-F-3052 | DCS | FLOW INDICATING CONTROLLER | 631-D-0305 DSL FUEL RECYC FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-FY -3052 | 631-F-3052 | VALVE | I/P CONVERTER | 631-G-0306A/B DSL FUEL PMP DISCH FLO | [14 empty] | HART AO | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-FAL -3052 | 631-F-3052 | DCS | FLOW ALARM LOW | 631-G-0306A/B DSL FUEL PMP DISCH FLO LO | [9 empty] | 14 |  |  | US gal/min |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3053 | 631-H-3053 | LP | HAND SWITCH | 631-LCP-4035 DSL FUEL TNK LVL ACK | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-HS -3057 | 631-H-3057 | LP | HAND SWITCH | 631-LCP-4035 LAMP TST | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-LIT -3052 | 631-L-3052 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0305 DSL FUEL TNK LVL | 6 | 135 | in | 0 | 100 | % | [7 empty] | 631-D-0305 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-XL -3052 | 631-L-3052 | LP | HIGH LEVEL LOCAL PANEL LIGHT | 631-LCP-4035 DSL FUEL TNK LVL HI | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-LI -3052 | 631-L-3052 | DCS | LEVEL INDICATION | 631-D-0305 DSL FUEL TNK LVL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LI -3052A | 631-L-3052 | LP | LOOP POWER INDICATOR | 631-LCP-4035 DSL FUEL TNK LVL | [14 empty] | AO | 631-DCS401 | 4-20mA | DCS | C | No | AUX
CA-741752-001 | 631-LAH -3052 | 631-L-3052 | DCS | LEVEL ALARM HIGH | 631-D-0305 DSL FUEL TNK LVL HI | [6 empty] | 83.7 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAL -3052 | 631-L-3052 | DCS | LEVEL ALARM LOW | 631-D-0305 DSL FUEL TNK LVL LO | [9 empty] | 14 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LIT -3054 | 631-L-3054 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0304A DSL FUEL FLTR LVL | 6 | 33.5 | in | 0 | 100 | % | [7 empty] | 631-D-0305 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-LIC -3054 | 631-L-3054 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0304A DSL FUEL FLTR LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAH -3054 | 631-L-3054 | DCS | LEVEL ALARM HIGH | 631-D-0304A DSL FUEL FLTR LVL HI | [6 empty] | 64.3 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAL -3054 | 631-L-3054 | DCS | LEVEL ALARM LOW | 631-D-0304A DSL FUEL FLTR LVL LO | [9 empty] | 11.6 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LIT -3055 | 631-L-3055 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0304B DSL FUEL FLTR LVL | 6 | 33.5 | in | 0 | 100 | % | [7 empty] | 631-D-0304B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-LIC -3055 | 631-L-3055 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0304B DSL FUEL FLTR LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAH -3055 | 631-L-3055 | DCS | LEVEL ALARM HIGH | 631-D-0304B DSL FUEL FLTR LVL HI | [6 empty] | 64.3 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAL -3055 | 631-L-3055 | DCS | LEVEL ALARM LOW | 631-D-0304B DSL FUEL FLTR LVL LO | [9 empty] | 11.6 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3060D | 631-M-3060 | MCC | DCS HAND SWITCH START | 631-G-0306A DSL FUEL PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-HS -3060E | 631-M-3060 | MCC | DCS HAND SWITCH STOP | 631-G-0306A DSL FUEL PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XA -3060A | 631-M-3060 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306A DSL FUEL PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XA -3060B | 631-M-3060 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306A DSL FUEL PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XI -3060 | 631-M-3060 | MCC | DCS INDICATION AUTO POSITION | 631-G-0306A DSL FUEL PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-HS -3061D | 631-M-3061 | MCC | DCS HAND SWITCH START | 631-G-0306B DSL FUEL PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-HS -3061E | 631-M-3061 | MCC | DCS HAND SWITCH STOP | 631-G-0306B DSL FUEL PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XA -3061A | 631-M-3061 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306B DSL FUEL PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XA -3061B | 631-M-3061 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306B DSL FUEL PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XI -3061 | 631-M-3061 | MCC | DCS INDICATION AUTO POSITION | 631-G-0306B DSL FUEL PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-PIT -3051 | 631-P-3051 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-D-0305 DSL FUEL TNK PR | 0 | 1 | psiG | 0 | 1 | psiG | [7 empty] | 631-D-0305 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PI -3051 | 631-P-3051 | DCS | DCS PRESSURE INDICATION | 631-D-0305 DSL FUEL TNK PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDIT -3053 | 631-P-3053 | FIELD | D/P TRANSMITTER | 631-D-0304A DSL FUEL FLTR DP | 0 | 80 | psi | 0 | 80 | psi | [7 empty] | 631-D-0304A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PDI -3053 | 631-P-3053 | DCS | DIFF PRESSURE INDICATION | 631-D-0304A DSL FUEL FLTR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDAH -3053 | 631-P-3053 | DCS | DIFF PRESSURE ALARM HIGH | 631-D-0304A DSL FUEL FLTR DP HI | [6 empty] | 9 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDIT -3054 | 631-P-3054 | FIELD | D/P TRANSMITTER | 631-D-0304B DSL FUEL FLTR DP | 0 | 80 | psi | 0 | 80 | psi | [7 empty] | 631-D-0304B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PDI -3054 | 631-P-3054 | DCS | DIFF PRESSURE INDICATION | 631-D-0304B DSL FUEL FLTR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDAH -3054 | 631-P-3054 | DCS | DIFF PRESSURE ALARM HIGH | 631-D-0304B DSL FUEL FLTR DP HI | [6 empty] | 9 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PIT -3057 | 631-P-3057 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0306A DSL FUEL PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PI -3057 | 631-P-3057 | DCS | DCS PRESSURE INDICATION | 631-G-0306A DSL FUEL PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PAH -3057 | 631-P-3057 | DCS | PRESSURE ALARM HIGH | 631-G-0306A DSL FUEL PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PIT -3058 | 631-P-3058 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0306B DSL FUEL PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PI -3058 | 631-P-3058 | DCS | DCS PRESSURE INDICATION | 631-G-0306B DSL FUEL PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PAH -3058 | 631-P-3058 | DCS | PRESSURE ALARM HIGH | 631-G-0306B DSL FUEL PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-TIT -3051 | 631-T-3051 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0306A DSL FUEL PMP DISCH TEMP | 0 | 160 | °F | 0 | 160 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-TI -3051 | 631-T-3051 | DCS | DCS TEMPERATURE INDICATION | 631-G-0306A DSL FUEL PMP DISCH TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-TIT -3052 | 631-T-3052 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0306B DSL FUEL PMP DISCH TEMP | 0 | 160 | °F | 0 | 160 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-TI -3052 | 631-T-3052 | DCS | DCS TEMPERATURE INDICATION | 631-G-0306B DSL FUEL PMP DISCH TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XR -3056 | 631-X-3056 | LP | LOCAL PANEL STROBE/HORN | 631-LCP-4035 DSL FUEL TNK LVL HI HORN | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-AY -0421 | 631-A-0421 | VALVE | SOLENOID VALVE | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-XSH -0421 | 631-A-0421 | VALVE | VALVE POSITION SWITCH OPEN | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741762-001 | 631-XSL -0421 | 631-A-0421 | VALVE | VALVE POSITION SWITCH CLOSED | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741762-001 | 631-XIH -0421 | 631-A-0421 | DCS | STATUS INDICATION OPEN | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-XIL -0421 | 631-A-0421 | DCS | STATUS INDICATION CLOSED | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0421A | 631-A-0421 | DCS | DCS HAND SWITCH VALVE OPEN | 631-G-0119A/B TO CRD SHIP PMP SUC HDR OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0421B | 631-A-0421 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-G-0119A/B TO CRD SHIP PMP SUC HDR CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-XA -0421 | 631-A-0421 | DCS | FAULT ALARM/TRIP INDICATION | 631-G-0119A/B TO CRD SHIP PMP SUC HDR FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-FIT -0421 | 631-F-0421 | FIELD | FLOW TRANSMITTER - VARIABLE AREA | 631-D-0118 CLS DRN DRM INL FG FLO | 2.8 | 28 | SCFM | 2.8 | 28 | SCFM | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-FI -0421 | 631-F-0421 | DCS | FLOW INDICATION | 631-D-0118 CLS DRN DRM INL FG FLO | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-FAL -0421 | 631-F-0421 | DCS | FLOW ALARM LOW | 631-D-0118 CLS DRN DRM INL FG FLO LO | [9 empty] | 15 |  |  | SCFM |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LIT -0421 | 631-L-0421 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0118 CLS DRN DRM LVL | 6 | 55 | in | 0 | 100 | % | [7 empty] | 631-D-0118 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-LIC -0421 | 631-L-0421 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0118 CLS DRN DRM LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LAH -0421 | 631-L-0421 | DCS | LEVEL ALARM HIGH | 631-D-0118 CLS DRN DRM LVL HI | [6 empty] | 85.8 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LAL -0421 | 631-L-0421 | DCS | LEVEL ALARM LOW | 631-D-0118 CLS DRN DRM LVL LO | [9 empty] | 24.5 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LY -0421 | 631-L-0421 | DCS | FUNCTION BLOCK | 631-D-0118 CLS DRN DRM LVL FNC BLK | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0421 | 631-L-0421 | DCS | DCS HAND SWITCH | 631-D-0119A/B CLS DRN PMP LEAD LAG SEL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0423D | 631-M-0423 | MCC | DCS HAND SWITCH START | 631-G-0119A CLS DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-HS -0423E | 631-M-0423 | MCC | DCS HAND SWITCH STOP | 631-G-0119A CLS DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-XA -0423A | 631-M-0423 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119A CLS DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XA -0423B | 631-M-0423 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119A CLS DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XI -0423 | 631-M-0423 | MCC | DCS INDICATION AUTO POSITION | 631-G-0119A CLS DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-HS -0424D | 631-M-0424 | MCC | DCS HAND SWITCH START | 631-G-0119B CLS DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-HS -0424E | 631-M-0424 | MCC | DCS HAND SWITCH STOP | 631-G-0119B CLS DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-XA -0424A | 631-M-0424 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119B CLS DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XA -0424B | 631-M-0424 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119B CLS DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XI -0424 | 631-M-0424 | MCC | DCS INDICATION AUTO POSITION | 631-G-0119B CLS DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-PIT -0424 | 631-P-0424 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP DISCH PR | 0 | 500 | psiG | 0 | 500 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PI -0424 | 631-P-0424 | DCS | DCS PRESSURE INDICATION | 631-G-0119A CLS DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAH -0424 | 631-P-0424 | DCS | PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP DISCH PR HI | [6 empty] | 305 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0424 | 631-P-0424 | DCS | PRESSURE ALARM LOW | 631-G-0119A CLS DRN PMP DISCH PR LO | [9 empty] | 257 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0425 | 631-P-0425 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP DISCH PR | 0 | 500 | psiG | 0 | 500 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PI -0425 | 631-P-0425 | DCS | DCS PRESSURE INDICATION | 631-G-0119B CLS DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAH -0425 | 631-P-0425 | DCS | PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP DISCH PR HI | [6 empty] | 305 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0425 | 631-P-0425 | DCS | PRESSURE ALARM LOW | 631-G-0119B CLS DRN PMP DISCH PR LO | [9 empty] | 257 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDIT -0429 | 631-P-0429 | FIELD | D/P TRANSMITTER | 631-G-0119A CLS DRN PMP SUC STNR DP | 0 | 2 | psi | 0 | 2 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PDI -0429 | 631-P-0429 | DCS | DIFF PRESSURE INDICATION | 631-G-0119A CLS DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDAH -0429 | 631-P-0429 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP SUC STNR DP HI | [6 empty] | 1 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDIT -0430 | 631-P-0430 | FIELD | D/P TRANSMITTER | 631-G-0119B CLS DRN PMP SUC STNR DP | 0 | 2 | psi | 0 | 2 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PDI -0430 | 631-P-0430 | DCS | DIFF PRESSURE INDICATION | 631-G-0119B CLS DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDAH -0430 | 631-P-0430 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP SUC STNR DP HI | [6 empty] | 1 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0431 | 631-P-0431 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A/B CLS DRN PMP DISCH PR | 0 | 500 | psiG | 0 | 500 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PI -0431 | 631-P-0431 | DCS | DCS PRESSURE INDICATION | 631-G-0119A/B CLS DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PY -0431 | 631-P-0431 | VALVE | I/P CONVERTER | 631-G-0119A/B MIN FLOW RECYC PR | [14 empty] | HART AO | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0431 | 631-P-0431 | DCS | PRESSURE ALARM HIGH | 631-G-0119A/B CLS DRN PMP DISCH PR HI | [6 empty] | 315 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIC -0431 | 631-P-0431 | DCS | PRESSURE INDICATION CONTROLLER | 631-G-0119A/B CLS DRN PMP DISCH PR CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0713 | 631-P-0713 | DCS | DCS PRESSURE INDICATION | 631-G-0119A CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0713 | 631-P-0713 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0713 | 631-P-0713 | DCS | PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0713 | 631-P-0713 | DCS | PRESSURE ALARM LOW | 631-G-0119A CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0714 | 631-P-0714 | DCS | DCS PRESSURE INDICATION | 631-G-0119B CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0714 | 631-P-0714 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0714 | 631-P-0714 | DCS | PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0714 | 631-P-0714 | DCS | PRESSURE ALARM LOW | 631-G-0119B CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0733 | 631-P-0733 | DCS | DCS PRESSURE INDICATION | 631-G-0119A CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0733 | 631-P-0733 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0733 | 631-P-0733 | DCS | PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0733 | 631-P-0733 | DCS | PRESSURE ALARM LOW | 631-G-0119A CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0734 | 631-P-0734 | DCS | DCS PRESSURE INDICATION | 631-G-0119B CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0734 | 631-P-0734 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0734 | 631-P-0734 | DCS | PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0734 | 631-P-0734 | DCS | PRESSURE ALARM LOW | 631-G-0119B CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0713 | 631-T-0713 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0713 | 631-T-0713 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119A CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0713A | 631-T-0713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0713B | 631-T-0713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0714 | 631-T-0714 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0714 | 631-T-0714 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119B CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0714A | 631-T-0714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0714B | 631-T-0714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0733 | 631-T-0733 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0733 | 631-T-0733 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119A CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0733A | 631-T-0733 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0733B | 631-T-0733 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0734 | 631-T-0734 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0734 | 631-T-0734 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119B CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0734A | 631-T-0734 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0734B | 631-T-0734 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-AY -0521 | 631-A-0521 | VALVE | SOLENOID VALVE | 631-D-0127 OW DRN DRM TO CD DRM OW VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-XSH -0521 | 631-A-0521 | VALVE | VALVE POSITION SWITCH OPEN | 631-D-0127 OW DRN DRM TO CD DRM OW VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741765-001 | 631-XSL -0521 | 631-A-0521 | VALVE | VALVE POSITION SWITCH CLOSED | 631-D-0127 OW DRN DRM TO CD DRM OW VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741765-001 | 631-XIH -0521 | 631-A-0521 | DCS | STATUS INDICATION OPEN | 631-D-0127 OW DRN DRM TO CD DRM OW VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XIL -0521 | 631-A-0521 | DCS | STATUS INDICATION CLOSED | 631-D-0127 OW DRN DRM TO CD DRM OW VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-HS -0521A | 631-A-0521 | DCS | DCS HAND SWITCH VALVE OPEN | 631-D-0127 OW DRN DRM TO CD DRM OW OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-HS -0521B | 631-A-0521 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-D-0127 OW DRN DRM TO CD DRM OW CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XA -0521 | 631-A-0521 | DCS | FAULT ALARM/TRIP INDICATION | 631-D-0127 OW DRN DRM TO CD DRM OW FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-FIT -0522 | 631-F-0522 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0128A/B OW DRN PMP DISCH FLO | 0 | 100 | inH2O | 0 | 110 | US gal/min | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-FIC -0522 | 631-F-0522 | DCS | FLOW INDICATING CONTROLLER | 631-G-0128A/B OW DRN PMP DISCH FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-FY -0522 | 631-F-0522 | VALVE | I/P CONVERTER | 631-G-0128A/B OW DRN PMP MIN FLO | [14 empty] | HART AO | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-HS -0521 | 631-H-0521 | DCS | DCS HANDSWITCH | 631-GD-0128A/B OW DRN PMP LEAD LAG SEL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LIT -0521 | 631-L-0521 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0127 OW DRN DRM LVL | 6 | 71 | in | 0 | 100 | % | [7 empty] | 631-D-0127 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-LIC -0521 | 631-L-0521 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0127 OW DRN DRM LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LAH -0521 | 631-L-0521 | DCS | LEVEL ALARM HIGH | 631-D-0127 OW DRN DRM LVL HI | [6 empty] | 87.1 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LAL -0521 | 631-L-0521 | DCS | LEVEL ALARM LOW | 631-D-0127 OW DRN DRM LVL LO | [9 empty] | 15.4 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LY -0521 | 631-L-0521 | DCS | FUNCTION BLOCK | 631-D-0127 OW DRN DRM LVL FNC BLK | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-HS -0523D | 631-M-0523 | MCC | DCS HAND SWITCH START | 631-G-0128A OW DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-HS -0523E | 631-M-0523 | MCC | DCS HAND SWITCH STOP | 631-G-0128A OW DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-XA -0523A | 631-M-0523 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128A OW DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XA -0523B | 631-M-0523 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128A OW DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XI -0523 | 631-M-0523 | MCC | DCS INDICATION AUTO POSITION | 631-G-0128A OW DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-HS -0524D | 631-M-0524 | MCC | DCS HAND SWITCH START | 631-G-0128B OW DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-HS -0524E | 631-M-0524 | MCC | DCS HAND SWITCH STOP | 631-G-0128B OW DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-XA -0524A | 631-M-0524 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128B OW DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XA -0524B | 631-M-0524 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128B OW DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XI -0524 | 631-M-0524 | MCC | DCS INDICATION AUTO POSITION | 631-G-0128B OW DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-PIT -0521 | 631-P-0521 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128A/B OW DRN PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PI -0521 | 631-P-0521 | DCS | DCS PRESSURE INDICATION | 631-G-0128A/B OW DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0524 | 631-P-0524 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128A OW DRN PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PI -0524 | 631-P-0524 | DCS | DCS PRESSURE INDICATION | 631-G-0128A OW DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAH -0524 | 631-P-0524 | DCS | PRESSURE ALARM HIGH | 631-G-0128A OW DRN PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0524 | 631-P-0524 | DCS | PRESSURE ALARM LOW | 631-G-0128A OW DRN PMP DISCH PR LO | [9 empty] | 15 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0525 | 631-P-0525 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128B OW DRN PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PI -0525 | 631-P-0525 | DCS | DCS PRESSURE INDICATION | 631-G-0128B OW DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAH -0525 | 631-P-0525 | DCS | PRESSURE ALARM HIGH | 631-G-0128B OW DRN PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0525 | 631-P-0525 | DCS | PRESSURE ALARM LOW | 631-G-0128B OW DRN PMP DISCH PR LO | [9 empty] | 15 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDIT -0528 | 631-P-0528 | FIELD | D/P TRANSMITTER | 631-G-0128A OW DRN PMP SUC STNR DP | 0 | 7 | psi | 0 | 7 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PDI -0528 | 631-P-0528 | DCS | DIFF PRESSURE INDICATION | 631-G-0128A OW DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDAH -0528 | 631-P-0528 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0128A OW DRN PMP SUC STNR DP HI | [6 empty] | 5 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDIT -0529 | 631-P-0529 | FIELD | D/P TRANSMITTER | 631-G-0128B OW DRN PMP SUC STNR DP | 0 | 7 | psi | 0 | 7 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PDI -0529 | 631-P-0529 | DCS | DIFF PRESSURE INDICATION | 631-G-0128B OW DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDAH -0529 | 631-P-0529 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0128B OW DRN PMP SUC STNR DP HI | [6 empty] | 5 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PI -0705 | 631-P-0705 | DCS | DCS PRESSURE INDICATION | 631-G-0128A OW DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0705 | 631-P-0705 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128A OW DRN PMP SEAL PR | 0 | 160 | psiG | 0 | 160 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PAH -0705 | 631-P-0705 | DCS | PRESSURE ALARM HIGH | 631-G-0128A OW DRN PMP SEAL PR HI | [6 empty] | 80 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0705 | 631-P-0705 | DCS | PRESSURE ALARM LOW | 631-G-0128A OW DRN PMP SEAL PR LO | [9 empty] | 30 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PI -0706 | 631-P-0706 | DCS | DCS PRESSURE INDICATION | 631-G-0128B OW DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0706 | 631-P-0706 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128B OW DRN PMP SEAL PR | 0 | 160 | psi | 0 | 160 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PAH -0706 | 631-P-0706 | DCS | PRESSURE ALARM HIGH | 631-G-0128B OW DRN PMP SEAL PR HI | [6 empty] | 80 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0706 | 631-P-0706 | DCS | PRESSURE ALARM LOW | 631-G-0128B OW DRN PMP SEAL PR LO | [9 empty] | 30 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TIT -0521 | 631-T-0521 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0128A/B OW DRN PMP DISCH TEMP | 0 | 160 | °F | 0 | 160 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-TI -0521 | 631-T-0521 | DCS | DCS TEMPERATURE INDICATION | 631-G-0128A/B OW DRN PMP DISCH TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TIT -0705 | 631-T-0705 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0128A OW DRN PMP SEAL TEMP | 0 | 230 | °F | 0 | 230 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-TI -0705 | 631-T-0705 | DCS | DCS TEMPERATURE INDICATION | 631-G-0128A OW DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0705A | 631-T-0705 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128A OW DRN PMP SEAL TEMP HI | [6 empty] | 176 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0705B | 631-T-0705 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128A OW DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TIT -0706 | 631-T-0706 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0128B OW DRN PMP SEAL TEMP | 0 | 230 | °F | 0 | 230 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-TI -0706 | 631-T-0706 | DCS | DCS TEMPERATURE INDICATION | 631-G-0128B OW DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0706A | 631-T-0706 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128B OW DRN PMP SEAL TEMP HI | [6 empty] | 176 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0706B | 631-T-0706 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128B OW DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVT -0705 | 631-X-0705 | FIELD | VIBRATION TRANSMITTER | 631-G-0128A OW DRN PMP VBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS401 | 4-20mA | DCS | C | No | AUX
CA-741765-001 | 631-XVAH -0705A | 631-X-0705 | DCS | VIBRATION ALARM HIGH | 631-G-0128A OW DRN PMP VBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVI -0705 | 631-X-0705 | DCS | VIBRATION INDICATION | 631-G-0128A OW DRN PMP VBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVAH -0705B | 631-X-0705 | DCS | VIBRATION ALARM HIGH | 631-G-0128A OW DRN PMP VBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVT -0706 | 631-X-0706 | FIELD | VIBRATION TRANSMITTER | 631-G-0128B OW DRN PMP VIBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS401 | 4-20mA | DCS | C | No | AUX
CA-741765-001 | 631-XVAH -0706A | 631-X-0706 | DCS | VIBRATION ALARM HIGH | 631-G-0128B OW DRN PMP VIBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVI -0706 | 631-X-0706 | DCS | VIBRATION INDICATION | 631-G-0128B OW DRN PMP VIBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVAH -0706B | 631-X-0706 | DCS | VIBRATION ALARM HIGH | 631-G-0128B OW DRN PMP VIBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FIT -3718 | 631-F-3718 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0262A POTABLE WTR PMP DISCH FLO | 0 | 200 | inH2O | 0 | 330 | US gal/min | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FIC -3718 | 631-F-3718 | DCS | FLOW INDICATING CONTROLLER | 631-G-0262A POTABLE WTR PMP DISCH FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FY -3718 | 631-F-3718 | VALVE | I/P CONVERTER | 631-G-0262A POTABLE WTR PMP MIN FLO | [14 empty] | HART AO | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FAL -3718 | 631-F-3718 | DCS | FLOW ALARM LOW | 631-G-0262A POTABLE WTR PMP DISCH FLO LO | [9 empty] | 105 |  |  | US gal/min |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FIT -3719 | 631-F-3719 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0262B POTABLE WTR PMP DISCH FLO | 0 | 200 | inH2O | 0 | 330 | US gal/min | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FIC -3719 | 631-F-3719 | DCS | FLOW INDICATING CONTROLLER | 631-G-0262B POTABLE WTR PMP DISCH FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FY -3719 | 631-F-3719 | VALVE | I/P CONVERTER | 631-G-0262B POTABLE WTR PMP MIN FLO | [14 empty] | HART AO | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FAL -3719 | 631-F-3719 | DCS | FLOW ALARM LOW | 631-G-0262B POTABLE WTR PMP DISCH FLO LO | [9 empty] | 105 |  |  | US gal/min |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-HS -3702 | 631-H-3702 | DCS | DCS HANDSWITCH | 631-G-0262A/B POTABLE WTR PMP DUTY SEL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-HS -3716D | 631-M-3716 | MCC | DCS HAND SWITCH START | 631-G-0262A POTABLE WTR PMP START | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-HS -3716E | 631-M-3716 | MCC | DCS HAND SWITCH STOP | 631-G-0262A POTABLE WTR PMP STP | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-XA -3716A | 631-M-3716 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262A POTABLE WTR PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XA -3716B | 631-M-3716 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262A POTABLE WTR PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XI -3716 | 631-M-3716 | MCC | DCS INDICATION AUTO POSITION | 631-G-0262A POTABLE WTR PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-HS -3717D | 631-M-3717 | MCC | DCS HAND SWITCH START | 631-G-0262B POTABLE WTR PMP START | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-HS -3717E | 631-M-3717 | MCC | DCS HAND SWITCH STOP | 631-G-0262B POTABLE WTR PMP STP | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-XA -3717A | 631-M-3717 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262B POTABLE WTR PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XA -3717B | 631-M-3717 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262B POTABLE WTR PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XI -3717 | 631-M-3717 | MCC | DCS INDICATION AUTO POSITION | 631-G-0262B POTABLE WTR PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-PIT -3714 | 631-P-3714 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP DISCH PR | 0 | 120 | psiG | 0 | 120 | psiG | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-PI -3714 | 631-P-3714 | DCS | DCS PRESSURE INDICATION | 631-G-0262A POTABLE WTR PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-PAL -3714 | 631-P-3714 | DCS | PRESSURE ALARM LOW | 631-G-0262A POTABLE WTR PMP DISCH PR LO | [9 empty] | 104 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-PIT -3715 | 631-P-3715 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP DISCH PR | 0 | 120 | psiG | 0 | 120 | psiG | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-PI -3715 | 631-P-3715 | DCS | DCS PRESSURE INDICATION | 631-G-0262B POTABLE WTR PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-PAL -3715 | 631-P-3715 | DCS | PRESSURE ALARM LOW | 631-G-0262B POTABLE WTR PMP DISCH PR LO | [9 empty] | 104 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3713 | 631-T-3713 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3713 | 631-T-3713 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3713A | 631-T-3713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3713B | 631-T-3713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3714 | 631-T-3714 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3714 | 631-T-3714 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3714A | 631-T-3714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3714B | 631-T-3714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3715 | 631-T-3715 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3715 | 631-T-3715 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3715A | 631-T-3715 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3715B | 631-T-3715 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3716 | 631-T-3716 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3716 | 631-T-3716 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3716A | 631-T-3716 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3716B | 631-T-3716 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3717 | 631-T-3717 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3717 | 631-T-3717 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3717A | 631-T-3717 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3717B | 631-T-3717 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3718 | 631-T-3718 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3718 | 631-T-3718 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3718A | 631-T-3718 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3718B | 631-T-3718 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVT -3718 | 631-X-3718 | FIELD | VIBRATION TRANSMITTER | 631-G-0262A POTABLE WTR PMP CASING VIBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS402 | 4-20mA | DCS | C | No | AUX
CA-741768-001 | 631-XVAH -3718A | 631-X-3718 | DCS | VIBRATION ALARM HIGH | 631-G-0262A POTABLE WTR PMP CASING VIBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVI -3718 | 631-X-3718 | DCS | VIBRATION INDICATION | 631-G-0262A POTABLE WTR PMP CASING VIBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVAH -3718B | 631-X-3718 | DCS | VIBRATION ALARM HIGH | 631-G-0262A POTABLE WTR PMP CASING VIBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVT -3719 | 631-X-3719 | FIELD | VIBRATION TRANSMITTER | 631-G-0262B POTABLE WTR PMP CASING VIBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS402 | 4-20mA | DCS | C | No | AUX
CA-741768-001 | 631-XVAH -3719A | 631-X-3719 | DCS | VIBRATION ALARM HIGH | 631-G-0262B POTABLE WTR PMP CASING VIBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVI -3719 | 631-X-3719 | DCS | VIBRATION INDICATION | 631-G-0262B POTABLE WTR PMP CASING VIBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVAH -3719B | 631-X-3719 | DCS | VIBRATION ALARM HIGH | 631-G-0262B POTABLE WTR PMP CASING VIBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX

## Summary
Project UNTANGLE - Selected P&ID IO Records
Sanitized training extract from the DCS IO List
Training System | P&ID Reference | Record Count
Closed Drain Drum and Pumps | CA-741762-001 | 78
Oily Water Drain Drum and Pumps | CA-741765-001 | 69
Diesel Fuel Storage and Pumps | CA-741752-001 | 67
Potable Water Pumps | CA-741768-001 | 57
Total |  | 271
Scope note | The Filtered IO sheet retains all 28 source columns and includes both physical I/O and relevant DCS software/derived records.

## Closed Drain
PID | Tag Number | Loop Name | Location | Instrument Type | Service | Calibration Range Min | Calibration Range Max | Calibration Range Units | DCS Range Min | DCS Range Max | DCS Range Units | Alarm High | Alarm High High | High High Trip | Alarm Low | Alarm Low Low | Low Low Trip | Alarm Units | Equipment Name | I/O Type Name | Controller No. | Signal Type | System Type | Device Protocol | Power Supply | Remarks | Rev
CA-741762-001 | 631-AY -0421 | 631-A-0421 | VALVE | SOLENOID VALVE | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-XSH -0421 | 631-A-0421 | VALVE | VALVE POSITION SWITCH OPEN | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741762-001 | 631-XSL -0421 | 631-A-0421 | VALVE | VALVE POSITION SWITCH CLOSED | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741762-001 | 631-XIH -0421 | 631-A-0421 | DCS | STATUS INDICATION OPEN | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-XIL -0421 | 631-A-0421 | DCS | STATUS INDICATION CLOSED | 631-G-0119A/B TO CRD SHIP PMP SUC HDR VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0421A | 631-A-0421 | DCS | DCS HAND SWITCH VALVE OPEN | 631-G-0119A/B TO CRD SHIP PMP SUC HDR OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0421B | 631-A-0421 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-G-0119A/B TO CRD SHIP PMP SUC HDR CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-XA -0421 | 631-A-0421 | DCS | FAULT ALARM/TRIP INDICATION | 631-G-0119A/B TO CRD SHIP PMP SUC HDR FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-FIT -0421 | 631-F-0421 | FIELD | FLOW TRANSMITTER - VARIABLE AREA | 631-D-0118 CLS DRN DRM INL FG FLO | 2.8 | 28 | SCFM | 2.8 | 28 | SCFM | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-FI -0421 | 631-F-0421 | DCS | FLOW INDICATION | 631-D-0118 CLS DRN DRM INL FG FLO | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-FAL -0421 | 631-F-0421 | DCS | FLOW ALARM LOW | 631-D-0118 CLS DRN DRM INL FG FLO LO | [9 empty] | 15 |  |  | SCFM |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LIT -0421 | 631-L-0421 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0118 CLS DRN DRM LVL | 6 | 55 | in | 0 | 100 | % | [7 empty] | 631-D-0118 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-LIC -0421 | 631-L-0421 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0118 CLS DRN DRM LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LAH -0421 | 631-L-0421 | DCS | LEVEL ALARM HIGH | 631-D-0118 CLS DRN DRM LVL HI | [6 empty] | 85.8 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LAL -0421 | 631-L-0421 | DCS | LEVEL ALARM LOW | 631-D-0118 CLS DRN DRM LVL LO | [9 empty] | 24.5 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-LY -0421 | 631-L-0421 | DCS | FUNCTION BLOCK | 631-D-0118 CLS DRN DRM LVL FNC BLK | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0421 | 631-L-0421 | DCS | DCS HAND SWITCH | 631-D-0119A/B CLS DRN PMP LEAD LAG SEL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-HS -0423D | 631-M-0423 | MCC | DCS HAND SWITCH START | 631-G-0119A CLS DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-HS -0423E | 631-M-0423 | MCC | DCS HAND SWITCH STOP | 631-G-0119A CLS DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-XA -0423A | 631-M-0423 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119A CLS DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XA -0423B | 631-M-0423 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119A CLS DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XI -0423 | 631-M-0423 | MCC | DCS INDICATION AUTO POSITION | 631-G-0119A CLS DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-HS -0424D | 631-M-0424 | MCC | DCS HAND SWITCH START | 631-G-0119B CLS DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-HS -0424E | 631-M-0424 | MCC | DCS HAND SWITCH STOP | 631-G-0119B CLS DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741762-001 | 631-XA -0424A | 631-M-0424 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119B CLS DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XA -0424B | 631-M-0424 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0119B CLS DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-XI -0424 | 631-M-0424 | MCC | DCS INDICATION AUTO POSITION | 631-G-0119B CLS DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741762-001 | 631-PIT -0424 | 631-P-0424 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP DISCH PR | 0 | 500 | psiG | 0 | 500 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PI -0424 | 631-P-0424 | DCS | DCS PRESSURE INDICATION | 631-G-0119A CLS DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAH -0424 | 631-P-0424 | DCS | PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP DISCH PR HI | [6 empty] | 305 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0424 | 631-P-0424 | DCS | PRESSURE ALARM LOW | 631-G-0119A CLS DRN PMP DISCH PR LO | [9 empty] | 257 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0425 | 631-P-0425 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP DISCH PR | 0 | 500 | psiG | 0 | 500 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PI -0425 | 631-P-0425 | DCS | DCS PRESSURE INDICATION | 631-G-0119B CLS DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAH -0425 | 631-P-0425 | DCS | PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP DISCH PR HI | [6 empty] | 305 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0425 | 631-P-0425 | DCS | PRESSURE ALARM LOW | 631-G-0119B CLS DRN PMP DISCH PR LO | [9 empty] | 257 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDIT -0429 | 631-P-0429 | FIELD | D/P TRANSMITTER | 631-G-0119A CLS DRN PMP SUC STNR DP | 0 | 2 | psi | 0 | 2 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PDI -0429 | 631-P-0429 | DCS | DIFF PRESSURE INDICATION | 631-G-0119A CLS DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDAH -0429 | 631-P-0429 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP SUC STNR DP HI | [6 empty] | 1 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDIT -0430 | 631-P-0430 | FIELD | D/P TRANSMITTER | 631-G-0119B CLS DRN PMP SUC STNR DP | 0 | 2 | psi | 0 | 2 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PDI -0430 | 631-P-0430 | DCS | DIFF PRESSURE INDICATION | 631-G-0119B CLS DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PDAH -0430 | 631-P-0430 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP SUC STNR DP HI | [6 empty] | 1 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0431 | 631-P-0431 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A/B CLS DRN PMP DISCH PR | 0 | 500 | psiG | 0 | 500 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PI -0431 | 631-P-0431 | DCS | DCS PRESSURE INDICATION | 631-G-0119A/B CLS DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PY -0431 | 631-P-0431 | VALVE | I/P CONVERTER | 631-G-0119A/B MIN FLOW RECYC PR | [14 empty] | HART AO | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0431 | 631-P-0431 | DCS | PRESSURE ALARM HIGH | 631-G-0119A/B CLS DRN PMP DISCH PR HI | [6 empty] | 315 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIC -0431 | 631-P-0431 | DCS | PRESSURE INDICATION CONTROLLER | 631-G-0119A/B CLS DRN PMP DISCH PR CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0713 | 631-P-0713 | DCS | DCS PRESSURE INDICATION | 631-G-0119A CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0713 | 631-P-0713 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0713 | 631-P-0713 | DCS | PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0713 | 631-P-0713 | DCS | PRESSURE ALARM LOW | 631-G-0119A CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0714 | 631-P-0714 | DCS | DCS PRESSURE INDICATION | 631-G-0119B CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0714 | 631-P-0714 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0714 | 631-P-0714 | DCS | PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0714 | 631-P-0714 | DCS | PRESSURE ALARM LOW | 631-G-0119B CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0733 | 631-P-0733 | DCS | DCS PRESSURE INDICATION | 631-G-0119A CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0733 | 631-P-0733 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0733 | 631-P-0733 | DCS | PRESSURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0733 | 631-P-0733 | DCS | PRESSURE ALARM LOW | 631-G-0119A CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PI -0734 | 631-P-0734 | DCS | DCS PRESSURE INDICATION | 631-G-0119B CLS DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PIT -0734 | 631-P-0734 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL PR | 0 | 60 | psiG | 0 | 60 | psiG | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741762-001 | 631-PAH -0734 | 631-P-0734 | DCS | PRESSURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL PR HI | [6 empty] | 40 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-PAL -0734 | 631-P-0734 | DCS | PRESSURE ALARM LOW | 631-G-0119B CLS DRN PMP SEAL PR LO | [9 empty] | 25 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0713 | 631-T-0713 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0713 | 631-T-0713 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119A CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0713A | 631-T-0713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0713B | 631-T-0713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0714 | 631-T-0714 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0714 | 631-T-0714 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119B CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0714A | 631-T-0714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0714B | 631-T-0714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0733 | 631-T-0733 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119A CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0733 | 631-T-0733 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119A CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0733A | 631-T-0733 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0733B | 631-T-0733 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119A CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TIT -0734 | 631-T-0734 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0119B CLS DRN PMP SEAL TEMP | 0 | 250 | °F | 0 | 250 | °F | [7 empty] | 631-G-0119B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741762-001 | 631-TI -0734 | 631-T-0734 | DCS | DCS TEMPERATURE INDICATION | 631-G-0119B CLS DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0734A | 631-T-0734 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741762-001 | 631-TAH -0734B | 631-T-0734 | DCS | TEMPERATURE ALARM HIGH | 631-G-0119B CLS DRN PMP SEAL TEMP HI | [6 empty] | 203 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX

## Oily Water
PID | Tag Number | Loop Name | Location | Instrument Type | Service | Calibration Range Min | Calibration Range Max | Calibration Range Units | DCS Range Min | DCS Range Max | DCS Range Units | Alarm High | Alarm High High | High High Trip | Alarm Low | Alarm Low Low | Low Low Trip | Alarm Units | Equipment Name | I/O Type Name | Controller No. | Signal Type | System Type | Device Protocol | Power Supply | Remarks | Rev
CA-741765-001 | 631-AY -0521 | 631-A-0521 | VALVE | SOLENOID VALVE | 631-D-0127 OW DRN DRM TO CD DRM OW VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-XSH -0521 | 631-A-0521 | VALVE | VALVE POSITION SWITCH OPEN | 631-D-0127 OW DRN DRM TO CD DRM OW VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741765-001 | 631-XSL -0521 | 631-A-0521 | VALVE | VALVE POSITION SWITCH CLOSED | 631-D-0127 OW DRN DRM TO CD DRM OW VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741765-001 | 631-XIH -0521 | 631-A-0521 | DCS | STATUS INDICATION OPEN | 631-D-0127 OW DRN DRM TO CD DRM OW VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XIL -0521 | 631-A-0521 | DCS | STATUS INDICATION CLOSED | 631-D-0127 OW DRN DRM TO CD DRM OW VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-HS -0521A | 631-A-0521 | DCS | DCS HAND SWITCH VALVE OPEN | 631-D-0127 OW DRN DRM TO CD DRM OW OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-HS -0521B | 631-A-0521 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-D-0127 OW DRN DRM TO CD DRM OW CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XA -0521 | 631-A-0521 | DCS | FAULT ALARM/TRIP INDICATION | 631-D-0127 OW DRN DRM TO CD DRM OW FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-FIT -0522 | 631-F-0522 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0128A/B OW DRN PMP DISCH FLO | 0 | 100 | inH2O | 0 | 110 | US gal/min | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-FIC -0522 | 631-F-0522 | DCS | FLOW INDICATING CONTROLLER | 631-G-0128A/B OW DRN PMP DISCH FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-FY -0522 | 631-F-0522 | VALVE | I/P CONVERTER | 631-G-0128A/B OW DRN PMP MIN FLO | [14 empty] | HART AO | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-HS -0521 | 631-H-0521 | DCS | DCS HANDSWITCH | 631-GD-0128A/B OW DRN PMP LEAD LAG SEL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LIT -0521 | 631-L-0521 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0127 OW DRN DRM LVL | 6 | 71 | in | 0 | 100 | % | [7 empty] | 631-D-0127 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-LIC -0521 | 631-L-0521 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0127 OW DRN DRM LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LAH -0521 | 631-L-0521 | DCS | LEVEL ALARM HIGH | 631-D-0127 OW DRN DRM LVL HI | [6 empty] | 87.1 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LAL -0521 | 631-L-0521 | DCS | LEVEL ALARM LOW | 631-D-0127 OW DRN DRM LVL LO | [9 empty] | 15.4 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-LY -0521 | 631-L-0521 | DCS | FUNCTION BLOCK | 631-D-0127 OW DRN DRM LVL FNC BLK | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-HS -0523D | 631-M-0523 | MCC | DCS HAND SWITCH START | 631-G-0128A OW DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-HS -0523E | 631-M-0523 | MCC | DCS HAND SWITCH STOP | 631-G-0128A OW DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-XA -0523A | 631-M-0523 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128A OW DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XA -0523B | 631-M-0523 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128A OW DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XI -0523 | 631-M-0523 | MCC | DCS INDICATION AUTO POSITION | 631-G-0128A OW DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-HS -0524D | 631-M-0524 | MCC | DCS HAND SWITCH START | 631-G-0128B OW DRN PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-HS -0524E | 631-M-0524 | MCC | DCS HAND SWITCH STOP | 631-G-0128B OW DRN PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741765-001 | 631-XA -0524A | 631-M-0524 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128B OW DRN PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XA -0524B | 631-M-0524 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0128B OW DRN PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-XI -0524 | 631-M-0524 | MCC | DCS INDICATION AUTO POSITION | 631-G-0128B OW DRN PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741765-001 | 631-PIT -0521 | 631-P-0521 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128A/B OW DRN PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PI -0521 | 631-P-0521 | DCS | DCS PRESSURE INDICATION | 631-G-0128A/B OW DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0524 | 631-P-0524 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128A OW DRN PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PI -0524 | 631-P-0524 | DCS | DCS PRESSURE INDICATION | 631-G-0128A OW DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAH -0524 | 631-P-0524 | DCS | PRESSURE ALARM HIGH | 631-G-0128A OW DRN PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0524 | 631-P-0524 | DCS | PRESSURE ALARM LOW | 631-G-0128A OW DRN PMP DISCH PR LO | [9 empty] | 15 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0525 | 631-P-0525 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128B OW DRN PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PI -0525 | 631-P-0525 | DCS | DCS PRESSURE INDICATION | 631-G-0128B OW DRN PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAH -0525 | 631-P-0525 | DCS | PRESSURE ALARM HIGH | 631-G-0128B OW DRN PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0525 | 631-P-0525 | DCS | PRESSURE ALARM LOW | 631-G-0128B OW DRN PMP DISCH PR LO | [9 empty] | 15 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDIT -0528 | 631-P-0528 | FIELD | D/P TRANSMITTER | 631-G-0128A OW DRN PMP SUC STNR DP | 0 | 7 | psi | 0 | 7 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PDI -0528 | 631-P-0528 | DCS | DIFF PRESSURE INDICATION | 631-G-0128A OW DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDAH -0528 | 631-P-0528 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0128A OW DRN PMP SUC STNR DP HI | [6 empty] | 5 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDIT -0529 | 631-P-0529 | FIELD | D/P TRANSMITTER | 631-G-0128B OW DRN PMP SUC STNR DP | 0 | 7 | psi | 0 | 7 | psi | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PDI -0529 | 631-P-0529 | DCS | DIFF PRESSURE INDICATION | 631-G-0128B OW DRN PMP SUC STNR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PDAH -0529 | 631-P-0529 | DCS | DIFF PRESSURE ALARM HIGH | 631-G-0128B OW DRN PMP SUC STNR DP HI | [6 empty] | 5 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PI -0705 | 631-P-0705 | DCS | DCS PRESSURE INDICATION | 631-G-0128A OW DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0705 | 631-P-0705 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128A OW DRN PMP SEAL PR | 0 | 160 | psiG | 0 | 160 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PAH -0705 | 631-P-0705 | DCS | PRESSURE ALARM HIGH | 631-G-0128A OW DRN PMP SEAL PR HI | [6 empty] | 80 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0705 | 631-P-0705 | DCS | PRESSURE ALARM LOW | 631-G-0128A OW DRN PMP SEAL PR LO | [9 empty] | 30 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PI -0706 | 631-P-0706 | DCS | DCS PRESSURE INDICATION | 631-G-0128B OW DRN PMP SEAL PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PIT -0706 | 631-P-0706 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0128B OW DRN PMP SEAL PR | 0 | 160 | psi | 0 | 160 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-PAH -0706 | 631-P-0706 | DCS | PRESSURE ALARM HIGH | 631-G-0128B OW DRN PMP SEAL PR HI | [6 empty] | 80 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-PAL -0706 | 631-P-0706 | DCS | PRESSURE ALARM LOW | 631-G-0128B OW DRN PMP SEAL PR LO | [9 empty] | 30 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TIT -0521 | 631-T-0521 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0128A/B OW DRN PMP DISCH TEMP | 0 | 160 | °F | 0 | 160 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-TI -0521 | 631-T-0521 | DCS | DCS TEMPERATURE INDICATION | 631-G-0128A/B OW DRN PMP DISCH TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TIT -0705 | 631-T-0705 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0128A OW DRN PMP SEAL TEMP | 0 | 230 | °F | 0 | 230 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-TI -0705 | 631-T-0705 | DCS | DCS TEMPERATURE INDICATION | 631-G-0128A OW DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0705A | 631-T-0705 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128A OW DRN PMP SEAL TEMP HI | [6 empty] | 176 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0705B | 631-T-0705 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128A OW DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TIT -0706 | 631-T-0706 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0128B OW DRN PMP SEAL TEMP | 0 | 230 | °F | 0 | 230 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741765-001 | 631-TI -0706 | 631-T-0706 | DCS | DCS TEMPERATURE INDICATION | 631-G-0128B OW DRN PMP SEAL TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0706A | 631-T-0706 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128B OW DRN PMP SEAL TEMP HI | [6 empty] | 176 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-TAH -0706B | 631-T-0706 | DCS | TEMPERATURE ALARM HIGH | 631-G-0128B OW DRN PMP SEAL TEMP HI | [6 empty] | 185 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVT -0705 | 631-X-0705 | FIELD | VIBRATION TRANSMITTER | 631-G-0128A OW DRN PMP VBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS401 | 4-20mA | DCS | C | No | AUX
CA-741765-001 | 631-XVAH -0705A | 631-X-0705 | DCS | VIBRATION ALARM HIGH | 631-G-0128A OW DRN PMP VBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVI -0705 | 631-X-0705 | DCS | VIBRATION INDICATION | 631-G-0128A OW DRN PMP VBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVAH -0705B | 631-X-0705 | DCS | VIBRATION ALARM HIGH | 631-G-0128A OW DRN PMP VBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVT -0706 | 631-X-0706 | FIELD | VIBRATION TRANSMITTER | 631-G-0128B OW DRN PMP VIBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS401 | 4-20mA | DCS | C | No | AUX
CA-741765-001 | 631-XVAH -0706A | 631-X-0706 | DCS | VIBRATION ALARM HIGH | 631-G-0128B OW DRN PMP VIBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVI -0706 | 631-X-0706 | DCS | VIBRATION INDICATION | 631-G-0128B OW DRN PMP VIBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741765-001 | 631-XVAH -0706B | 631-X-0706 | DCS | VIBRATION ALARM HIGH | 631-G-0128B OW DRN PMP VIBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX

## Diesel Fuel
PID | Tag Number | Loop Name | Location | Instrument Type | Service | Calibration Range Min | Calibration Range Max | Calibration Range Units | DCS Range Min | DCS Range Max | DCS Range Units | Alarm High | Alarm High High | High High Trip | Alarm Low | Alarm Low Low | Low Low Trip | Alarm Units | Equipment Name | I/O Type Name | Controller No. | Signal Type | System Type | Device Protocol | Power Supply | Remarks | Rev
CA-741752-001 | 631-AY -3054 | 631-A-3054 | VALVE | SOLENOID VALVE | 631-D-0304A DSL FUEL FLTR DRN VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XSH -3054 | 631-A-3054 | VALVE | VALVE POSITION SWITCH OPEN | 631-D-0304A DSL FUEL FLTR DRN VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XSL -3054 | 631-A-3054 | VALVE | VALVE POSITION SWITCH CLOSED | 631-D-0304A DSL FUEL FLTR DRN VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XIH -3054 | 631-A-3054 | DCS | STATUS INDICATION OPEN | 631-D-0304A DSL FUEL FLTR DRN VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XIL -3054 | 631-A-3054 | DCS | STATUS INDICATION CLOSED | 631-D-0304A DSL FUEL FLTR DRN VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3054A | 631-A-3054 | DCS | DCS HAND SWITCH VALVE OPEN | 631-D-0304A DSL FUEL FLTR DRN OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3054B | 631-A-3054 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-D-0304A DSL FUEL FLTR DRN CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XA -3054 | 631-A-3054 | DCS | FAULT ALARM/TRIP INDICATION | 631-D-0304A DSL FUEL FLTR DRN FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-AY -3055 | 631-A-3055 | VALVE | SOLENOID VALVE | 631-D-0304B DSL FUEL FLTR DRN VLV | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XSH -3055 | 631-A-3055 | VALVE | VALVE POSITION SWITCH OPEN | 631-D-0304B DSL FUEL FLTR DRN VLV OPN | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XSL -3055 | 631-A-3055 | VALVE | VALVE POSITION SWITCH CLOSED | 631-D-0304B DSL FUEL FLTR DRN VLV CLS | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-XIH -3055 | 631-A-3055 | DCS | STATUS INDICATION OPEN | 631-D-0304B DSL FUEL FLTR DRN VLV OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XIL -3055 | 631-A-3055 | DCS | STATUS INDICATION CLOSED | 631-D-0304B DSL FUEL FLTR DRN VLV CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3055A | 631-A-3055 | DCS | DCS HAND SWITCH VALVE OPEN | 631-D-0304B DSL FUEL FLTR DRN OPN | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3055B | 631-A-3055 | DCS | DCS HAND SWITCH VALVE CLOSE | 631-D-0304B DSL FUEL FLTR DRN CLS | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XA -3055 | 631-A-3055 | DCS | FAULT ALARM/TRIP INDICATION | 631-D-0304B DSL FUEL FLTR DRN FLT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-FIT -3051 | 631-F-3051 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-D-0305 DSL FUEL TNK INL FLO | 0 | 100 | inH2O | 0 | 110 | US gal/min | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-FQI -3051 | 631-F-3051 | DCS | FLOW TOTALIZING INDICATOR | 631-D-0305 DSL FUEL TNK INL FLO TOT | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-FIT -3052 | 631-F-3052 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0306A/B DSL FUEL PMP DISCH FLO | 0 | 100 | inH2O | 0 | 45 | US gal/min | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-FIC -3052 | 631-F-3052 | DCS | FLOW INDICATING CONTROLLER | 631-D-0305 DSL FUEL RECYC FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-FY -3052 | 631-F-3052 | VALVE | I/P CONVERTER | 631-G-0306A/B DSL FUEL PMP DISCH FLO | [14 empty] | HART AO | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-FAL -3052 | 631-F-3052 | DCS | FLOW ALARM LOW | 631-G-0306A/B DSL FUEL PMP DISCH FLO LO | [9 empty] | 14 |  |  | US gal/min |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3053 | 631-H-3053 | LP | HAND SWITCH | 631-LCP-4035 DSL FUEL TNK LVL ACK | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-HS -3057 | 631-H-3057 | LP | HAND SWITCH | 631-LCP-4035 LAMP TST | [14 empty] | DI | 631-DCS401 | FREE | DCS | C | No | AUX
CA-741752-001 | 631-LIT -3052 | 631-L-3052 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0305 DSL FUEL TNK LVL | 6 | 135 | in | 0 | 100 | % | [7 empty] | 631-D-0305 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-XL -3052 | 631-L-3052 | LP | HIGH LEVEL LOCAL PANEL LIGHT | 631-LCP-4035 DSL FUEL TNK LVL HI | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-LI -3052 | 631-L-3052 | DCS | LEVEL INDICATION | 631-D-0305 DSL FUEL TNK LVL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LI -3052A | 631-L-3052 | LP | LOOP POWER INDICATOR | 631-LCP-4035 DSL FUEL TNK LVL | [14 empty] | AO | 631-DCS401 | 4-20mA | DCS | C | No | AUX
CA-741752-001 | 631-LAH -3052 | 631-L-3052 | DCS | LEVEL ALARM HIGH | 631-D-0305 DSL FUEL TNK LVL HI | [6 empty] | 83.7 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAL -3052 | 631-L-3052 | DCS | LEVEL ALARM LOW | 631-D-0305 DSL FUEL TNK LVL LO | [9 empty] | 14 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LIT -3054 | 631-L-3054 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0304A DSL FUEL FLTR LVL | 6 | 33.5 | in | 0 | 100 | % | [7 empty] | 631-D-0305 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-LIC -3054 | 631-L-3054 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0304A DSL FUEL FLTR LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAH -3054 | 631-L-3054 | DCS | LEVEL ALARM HIGH | 631-D-0304A DSL FUEL FLTR LVL HI | [6 empty] | 64.3 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAL -3054 | 631-L-3054 | DCS | LEVEL ALARM LOW | 631-D-0304A DSL FUEL FLTR LVL LO | [9 empty] | 11.6 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LIT -3055 | 631-L-3055 | FIELD | LEVEL TRANSMITTER GUIDED WAVE RADAR | 631-D-0304B DSL FUEL FLTR LVL | 6 | 33.5 | in | 0 | 100 | % | [7 empty] | 631-D-0304B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-LIC -3055 | 631-L-3055 | DCS | LEVEL INDICATION CONTROLLER | 631-D-0304B DSL FUEL FLTR LVL CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAH -3055 | 631-L-3055 | DCS | LEVEL ALARM HIGH | 631-D-0304B DSL FUEL FLTR LVL HI | [6 empty] | 64.3 | [5 empty] | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-LAL -3055 | 631-L-3055 | DCS | LEVEL ALARM LOW | 631-D-0304B DSL FUEL FLTR LVL LO | [9 empty] | 11.6 |  |  | % |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-HS -3060D | 631-M-3060 | MCC | DCS HAND SWITCH START | 631-G-0306A DSL FUEL PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-HS -3060E | 631-M-3060 | MCC | DCS HAND SWITCH STOP | 631-G-0306A DSL FUEL PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XA -3060A | 631-M-3060 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306A DSL FUEL PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XA -3060B | 631-M-3060 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306A DSL FUEL PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XI -3060 | 631-M-3060 | MCC | DCS INDICATION AUTO POSITION | 631-G-0306A DSL FUEL PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-HS -3061D | 631-M-3061 | MCC | DCS HAND SWITCH START | 631-G-0306B DSL FUEL PMP START | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-HS -3061E | 631-M-3061 | MCC | DCS HAND SWITCH STOP | 631-G-0306B DSL FUEL PMP STP | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX
CA-741752-001 | 631-XA -3061A | 631-M-3061 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306B DSL FUEL PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XA -3061B | 631-M-3061 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0306B DSL FUEL PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-XI -3061 | 631-M-3061 | MCC | DCS INDICATION AUTO POSITION | 631-G-0306B DSL FUEL PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741752-001 | 631-PIT -3051 | 631-P-3051 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-D-0305 DSL FUEL TNK PR | 0 | 1 | psiG | 0 | 1 | psiG | [7 empty] | 631-D-0305 | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PI -3051 | 631-P-3051 | DCS | DCS PRESSURE INDICATION | 631-D-0305 DSL FUEL TNK PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDIT -3053 | 631-P-3053 | FIELD | D/P TRANSMITTER | 631-D-0304A DSL FUEL FLTR DP | 0 | 80 | psi | 0 | 80 | psi | [7 empty] | 631-D-0304A | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PDI -3053 | 631-P-3053 | DCS | DIFF PRESSURE INDICATION | 631-D-0304A DSL FUEL FLTR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDAH -3053 | 631-P-3053 | DCS | DIFF PRESSURE ALARM HIGH | 631-D-0304A DSL FUEL FLTR DP HI | [6 empty] | 9 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDIT -3054 | 631-P-3054 | FIELD | D/P TRANSMITTER | 631-D-0304B DSL FUEL FLTR DP | 0 | 80 | psi | 0 | 80 | psi | [7 empty] | 631-D-0304B | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PDI -3054 | 631-P-3054 | DCS | DIFF PRESSURE INDICATION | 631-D-0304B DSL FUEL FLTR DP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PDAH -3054 | 631-P-3054 | DCS | DIFF PRESSURE ALARM HIGH | 631-D-0304B DSL FUEL FLTR DP HI | [6 empty] | 9 | [5 empty] | psi |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PIT -3057 | 631-P-3057 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0306A DSL FUEL PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PI -3057 | 631-P-3057 | DCS | DCS PRESSURE INDICATION | 631-G-0306A DSL FUEL PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PAH -3057 | 631-P-3057 | DCS | PRESSURE ALARM HIGH | 631-G-0306A DSL FUEL PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PIT -3058 | 631-P-3058 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0306B DSL FUEL PMP DISCH PR | 0 | 150 | psiG | 0 | 150 | psiG | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-PI -3058 | 631-P-3058 | DCS | DCS PRESSURE INDICATION | 631-G-0306B DSL FUEL PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-PAH -3058 | 631-P-3058 | DCS | PRESSURE ALARM HIGH | 631-G-0306B DSL FUEL PMP DISCH PR HI | [6 empty] | 105 | [5 empty] | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-TIT -3051 | 631-T-3051 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0306A DSL FUEL PMP DISCH TEMP | 0 | 160 | °F | 0 | 160 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-TI -3051 | 631-T-3051 | DCS | DCS TEMPERATURE INDICATION | 631-G-0306A DSL FUEL PMP DISCH TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-TIT -3052 | 631-T-3052 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0306B DSL FUEL PMP DISCH TEMP | 0 | 160 | °F | 0 | 160 | °F | [8 empty] | HART AI | 631-DCS401 | 4-20mA | DCS | H | No | AUX
CA-741752-001 | 631-TI -3052 | 631-T-3052 | DCS | DCS TEMPERATURE INDICATION | 631-G-0306B DSL FUEL PMP DISCH TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741752-001 | 631-XR -3056 | 631-X-3056 | LP | LOCAL PANEL STROBE/HORN | 631-LCP-4035 DSL FUEL TNK LVL HI HORN | [14 empty] | DO | 631-DCS401 | 24VDC | DCS | C | No | AUX

## Potable Water
PID | Tag Number | Loop Name | Location | Instrument Type | Service | Calibration Range Min | Calibration Range Max | Calibration Range Units | DCS Range Min | DCS Range Max | DCS Range Units | Alarm High | Alarm High High | High High Trip | Alarm Low | Alarm Low Low | Low Low Trip | Alarm Units | Equipment Name | I/O Type Name | Controller No. | Signal Type | System Type | Device Protocol | Power Supply | Remarks | Rev
CA-741768-001 | 631-FIT -3718 | 631-F-3718 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0262A POTABLE WTR PMP DISCH FLO | 0 | 200 | inH2O | 0 | 330 | US gal/min | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FIC -3718 | 631-F-3718 | DCS | FLOW INDICATING CONTROLLER | 631-G-0262A POTABLE WTR PMP DISCH FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FY -3718 | 631-F-3718 | VALVE | I/P CONVERTER | 631-G-0262A POTABLE WTR PMP MIN FLO | [14 empty] | HART AO | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FAL -3718 | 631-F-3718 | DCS | FLOW ALARM LOW | 631-G-0262A POTABLE WTR PMP DISCH FLO LO | [9 empty] | 105 |  |  | US gal/min |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FIT -3719 | 631-F-3719 | FIELD | FLOW INDICATING TRANSMITTER - D/P | 631-G-0262B POTABLE WTR PMP DISCH FLO | 0 | 200 | inH2O | 0 | 330 | US gal/min | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FIC -3719 | 631-F-3719 | DCS | FLOW INDICATING CONTROLLER | 631-G-0262B POTABLE WTR PMP DISCH FLO CTRL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-FY -3719 | 631-F-3719 | VALVE | I/P CONVERTER | 631-G-0262B POTABLE WTR PMP MIN FLO | [14 empty] | HART AO | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-FAL -3719 | 631-F-3719 | DCS | FLOW ALARM LOW | 631-G-0262B POTABLE WTR PMP DISCH FLO LO | [9 empty] | 105 |  |  | US gal/min |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-HS -3702 | 631-H-3702 | DCS | DCS HANDSWITCH | 631-G-0262A/B POTABLE WTR PMP DUTY SEL | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-HS -3716D | 631-M-3716 | MCC | DCS HAND SWITCH START | 631-G-0262A POTABLE WTR PMP START | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-HS -3716E | 631-M-3716 | MCC | DCS HAND SWITCH STOP | 631-G-0262A POTABLE WTR PMP STP | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-XA -3716A | 631-M-3716 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262A POTABLE WTR PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XA -3716B | 631-M-3716 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262A POTABLE WTR PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XI -3716 | 631-M-3716 | MCC | DCS INDICATION AUTO POSITION | 631-G-0262A POTABLE WTR PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-HS -3717D | 631-M-3717 | MCC | DCS HAND SWITCH START | 631-G-0262B POTABLE WTR PMP START | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-HS -3717E | 631-M-3717 | MCC | DCS HAND SWITCH STOP | 631-G-0262B POTABLE WTR PMP STP | [14 empty] | DO | 631-DCS402 | 24VDC | DCS | C | No | AUX
CA-741768-001 | 631-XA -3717A | 631-M-3717 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262B POTABLE WTR PMP FLT | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XA -3717B | 631-M-3717 | MCC | FAULT ALARM/TRIP INDICATION | 631-G-0262B POTABLE WTR PMP TRP | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-XI -3717 | 631-M-3717 | MCC | DCS INDICATION AUTO POSITION | 631-G-0262B POTABLE WTR PMP AUTO POSITION | [14 empty] | SID |  | SERIAL | DCS | M | No | AUX
CA-741768-001 | 631-PIT -3714 | 631-P-3714 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP DISCH PR | 0 | 120 | psiG | 0 | 120 | psiG | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-PI -3714 | 631-P-3714 | DCS | DCS PRESSURE INDICATION | 631-G-0262A POTABLE WTR PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-PAL -3714 | 631-P-3714 | DCS | PRESSURE ALARM LOW | 631-G-0262A POTABLE WTR PMP DISCH PR LO | [9 empty] | 104 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-PIT -3715 | 631-P-3715 | FIELD | PRESSURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP DISCH PR | 0 | 120 | psiG | 0 | 120 | psiG | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX
CA-741768-001 | 631-PI -3715 | 631-P-3715 | DCS | DCS PRESSURE INDICATION | 631-G-0262B POTABLE WTR PMP DISCH PR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-PAL -3715 | 631-P-3715 | DCS | PRESSURE ALARM LOW | 631-G-0262B POTABLE WTR PMP DISCH PR LO | [9 empty] | 104 |  |  | psiG |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3713 | 631-T-3713 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3713 | 631-T-3713 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3713A | 631-T-3713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3713B | 631-T-3713 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3714 | 631-T-3714 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3714 | 631-T-3714 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3714A | 631-T-3714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3714B | 631-T-3714 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP THRUST BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3715 | 631-T-3715 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3715 | 631-T-3715 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3715A | 631-T-3715 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3715B | 631-T-3715 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3716 | 631-T-3716 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3716 | 631-T-3716 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3716A | 631-T-3716 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3716B | 631-T-3716 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262A POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3717 | 631-T-3717 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3717 | 631-T-3717 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3717A | 631-T-3717 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3717B | 631-T-3717 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP RAD BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TI -3718 | 631-T-3718 | DCS | DCS TEMPERATURE INDICATION | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TIT -3718 | 631-T-3718 | FIELD | TEMPERATURE INDICATING TRANSMITTER | 631-G-0262B POTABLE WTR PMP THURST BRNG TMEP | 0 | 250 | °F | 0 | 250 | °F | [8 empty] | HART AI | 631-DCS402 | 4-20mA | DCS | H | No | AUX | Rev 00d
CA-741768-001 | 631-TAH -3718A | 631-T-3718 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TEMP HI | [6 empty] | 200 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-TAH -3718B | 631-T-3718 | DCS | TEMPERATURE ALARM HIGH | 631-G-0262B POTABLE WTR PMP THURST BRNG TEMP HI | [6 empty] | 220 | [5 empty] | °F |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVT -3718 | 631-X-3718 | FIELD | VIBRATION TRANSMITTER | 631-G-0262A POTABLE WTR PMP CASING VIBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS402 | 4-20mA | DCS | C | No | AUX
CA-741768-001 | 631-XVAH -3718A | 631-X-3718 | DCS | VIBRATION ALARM HIGH | 631-G-0262A POTABLE WTR PMP CASING VIBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVI -3718 | 631-X-3718 | DCS | VIBRATION INDICATION | 631-G-0262A POTABLE WTR PMP CASING VIBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVAH -3718B | 631-X-3718 | DCS | VIBRATION ALARM HIGH | 631-G-0262A POTABLE WTR PMP CASING VIBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVT -3719 | 631-X-3719 | FIELD | VIBRATION TRANSMITTER | 631-G-0262B POTABLE WTR PMP CASING VIBR | 0 | 25.4 | mm/s | 0 | 25.4 | mm/s | [8 empty] | AI | 631-DCS402 | 4-20mA | DCS | C | No | AUX
CA-741768-001 | 631-XVAH -3719A | 631-X-3719 | DCS | VIBRATION ALARM HIGH | 631-G-0262B POTABLE WTR PMP CASING VIBR HI | [6 empty] | 7.6 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVI -3719 | 631-X-3719 | DCS | VIBRATION INDICATION | 631-G-0262B POTABLE WTR PMP CASING VIBR | [14 empty] | SW |  | - | DCS | - | No | AUX
CA-741768-001 | 631-XVAH -3719B | 631-X-3719 | DCS | VIBRATION ALARM HIGH | 631-G-0262B POTABLE WTR PMP CASING VIBR HI | [6 empty] | 12.7 | [5 empty] | mm/s |  | SW |  | - | DCS | - | No | AUX